## Read me
Joint Commission EC and LS to PE Crosswalk 2026 (Hospital program)
Complete line-by-line crosswalk built from the official Disposition Report. Updated October 2026.
WHAT THIS IS
Purpose | A searchable crosswalk showing where every former Environment of Care (EC) and Life Safety (LS) element of performance (EP) went in the 2026 Physical Environment (PE), National Performance Goals (NPG) and Human Resources (HR) chapters, for hospitals.
Coverage | All 463 former EC and LS EPs (195 EC, 268 LS) in the Joint Commission's Disposition Report for the Hospital program. Two EPs were split across two new EPs, so the Crosswalk tab has 465 rows.
Summaries | Requirement descriptions are short LeanSite summaries, not the official text. Rows marked 'Covers:' list the main subjects of the former EP. Code references are the NFPA sections the former EP cited. Use the Disposition Report or E-dition for exact wording.
March 2026 | The Notes column flags the March 1, 2026 revisions to PE.04.01.01 EP 1 and EP 2 and PE.04.01.03 EP 3.
HOW TO USE
Find an old EP | Filter the Crosswalk tab, or press Ctrl+F and type the old number (for example LS.02.01.35 EP 4).
Update your tools | Replace old numbers in policies, rounding tools, maintenance task names and survey binders with the New standard/EP column.
DISPOSITION TYPES
Moved | Same requirement, new number.
Moved and revised | New number with revised wording.
Consolidated | Several former EPs combined into one new EP.
Split | One former EP divided across two new EPs.
Deleted EP; replaced or moved to SPG | Former EP removed; the expectation is covered by a more direct EP that matches CMS language, with details in the Survey Process Guide (SPG).
Deleted | Removed with no new EP.
SOURCES
Disposition Report | Joint Commission. Disposition of Changes for the Hospital Program, Prepublication Standards, effective January 1, 2026 (version dated October 24, 2025). https://digitalassets.jointcommission.org/api/public/content/c583e3d14bb249e4accd13291c716557
March 2026 revisions | Joint Commission. Prepublication Requirements: Requirement Revisions Related to NFPA Codes and CMS CoPs, issued January 30, 2026, effective March 1, 2026. https://digitalassets.jointcommission.org/api/public/content/b56114d01df14bf18e39734a332d457d
Disclaimer | Educational reference from LeanSite. Not a substitute for the official Joint Commission manual or advice from your accreditation team.
KEEP IT ALL IN ONE PLACE
LeanSite | Schedule recurring ITM work across every location, with photos, dates and results saved on each job. getleansite.com
See it live | Book a demo with our team
Pair it with | PE Survey Readiness Checklist 2026 and PE Maintenance Compliance Calendar 2026.

## Crosswalk
EC and LS to PE Crosswalk
465 rows covering all 463 former EC and LS EPs. Filter any column.
Former standard / EP | Section | Former requirement (summary) | NFPA references cited | Disposition | New standard / EP | New requirement (summary) | Notes | Report page
EC.01.01.01 EP 1 | Planning and managing the environment | Leaders identify individuals to manage environmental risk |  | Deleted | N/A | No new EP |  | 1
EC.01.01.01 EP 3 | Planning and managing the environment | Library of inspection, testing and maintenance information |  | Deleted | N/A | No new EP |  | 1
EC.01.01.01 EP 4 | Planning and managing the environment | Written plan: environmental safety |  | Deleted | N/A | No new EP |  | 2
EC.01.01.01 EP 5 | Planning and managing the environment | Written plan: security |  | Deleted | N/A | No new EP |  | 2
EC.01.01.01 EP 6 | Planning and managing the environment | Written plan: hazardous materials and waste |  | Deleted | N/A | No new EP |  | 2
EC.01.01.01 EP 7 | Planning and managing the environment | Written plan: fire safety |  | Deleted | N/A | No new EP |  | 2
EC.01.01.01 EP 8 | Planning and managing the environment | Written plan: medical equipment |  | Deleted | N/A | No new EP |  | 2
EC.01.01.01 EP 9 | Planning and managing the environment | Written plan: utility systems |  | Deleted | N/A | No new EP |  | 2
EC.01.01.01 EP 12 | Planning and managing the environment | Comply with NFPA 99-2012 Health Care Facilities Code |  | Moved and revised | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 2
EC.02.01.01 EP 1 | Safety and security risks | Process to identify safety and security risks |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.01.01.01 EP 1 | Building constructed, arranged and maintained for safe access and patient safety |  | 2
EC.02.01.01 EP 3 | Safety and security risks | Act to minimize or eliminate identified risks |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.01.01.01 EP 1 | Building constructed, arranged and maintained for safe access and patient safety |  | 3
EC.02.01.01 EP 5 | Safety and security risks | Maintain all grounds and equipment |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.01.01.01 EP 1 | Building constructed, arranged and maintained for safe access and patient safety |  | 3
EC.02.01.01 EP 7 | Safety and security risks | Identify individuals entering the facilities |  | Deleted | N/A | No new EP |  | 3
EC.02.01.01 EP 8 | Safety and security risks | Control access to security-sensitive areas |  | Moved | NPG.11.01.01 EP 1 | Controls access to security-sensitive areas |  | 3
EC.02.01.01 EP 9 | Safety and security risks | Written security incident procedures, including infant or pediatric abduction |  | Consolidated (EC.02.01.01, EP 9; EC.02.01.01, EP 10) | NPG.11.01.01 EP 2 | Security incident policies and procedures, including infant or pediatric abduction |  | 3
EC.02.01.01 EP 10 | Safety and security risks | Follow procedures when a security incident occurs |  | Consolidated (EC.02.01.01, EP 9; EC.02.01.01, EP 10) | NPG.11.01.01 EP 2 | Security incident policies and procedures, including infant or pediatric abduction |  | 3
EC.02.01.01 EP 11 | Safety and security risks | Respond to product notices and recalls |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | N/A | No new EP |  | 4
EC.02.01.01 EP 14 | Safety and security risks | Manage MRI safety risks (patients, implants, ferromagnetic objects, noise) |  | Moved | NPG.13.03.01 EP 1 | MRI safety risks |  | 4
EC.02.01.01 EP 16 | Safety and security risks | Restrict MRI access, supervise restricted zones, post signage |  | Moved | NPG.13.03.01 EP 2 | MRI access restriction, supervision and signage |  | 4
EC.02.01.01 EP 17 | Safety and security risks | Annual workplace violence worksite analysis |  | Moved | NPG.02.04.01 EP 3 | Annual workplace violence worksite analysis |  | 4
EC.02.01.03 EP 4 | Smoking and oxygen ignition sources | Smoking materials and ignition sources around oxygen use | NFPA 99-2012: 11.5.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 4
EC.02.01.03 EP 6 | Smoking and oxygen ignition sources | Maintain compliance with smoking policy |  | Deleted | N/A | No new EP |  | 4
EC.02.02.01 EP 1 | Hazardous materials and waste | Inventory of hazardous materials and waste |  | Moved | PE.02.01.01 EP 1 | Written, current inventory of hazardous materials and waste |  | 5
EC.02.02.01 EP 3 | Hazardous materials and waste | Spill and exposure procedures, precautions and PPE |  | Consolidated (EC.02.02.01, EP 3; EC.02.02.01, EP 4; EC.02.02.01, EP 5; EC.02.02.01, EP 6; EC.02.02.01, EP 7; EC.02.02.01, EP 8; EC.02.02.01, EP 9) | PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure |  | 5
EC.02.02.01 EP 4 | Hazardous materials and waste | Implement spill and exposure procedures |  | Consolidated (EC.02.02.01, EP 3; EC.02.02.01, EP 4; EC.02.02.01, EP 5; EC.02.02.01, EP 6; EC.02.02.01, EP 7; EC.02.02.01, EP 8; EC.02.02.01, EP 9) | PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure |  | 5
EC.02.02.01 EP 5 | Hazardous materials and waste | Hazardous chemicals: selecting, handling, storing, using, disposing |  | Consolidated (EC.02.02.01, EP 3; EC.02.02.01, EP 4; EC.02.02.01, EP 5; EC.02.02.01, EP 6; EC.02.02.01, EP 7; EC.02.02.01, EP 8; EC.02.02.01, EP 9) | PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure |  | 6
EC.02.02.01 EP 6 | Hazardous materials and waste | Radioactive materials |  | Consolidated (EC.02.02.01, EP 3; EC.02.02.01, EP 4; EC.02.02.01, EP 5; EC.02.02.01, EP 6; EC.02.02.01, EP 7; EC.02.02.01, EP 8; EC.02.02.01, EP 9) | PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure |  | 6
EC.02.02.01 EP 7 | Hazardous materials and waste | Hazardous energy sources, including shielding |  | Consolidated (EC.02.02.01, EP 3; EC.02.02.01, EP 4; EC.02.02.01, EP 5; EC.02.02.01, EP 6; EC.02.02.01, EP 7; EC.02.02.01, EP 8; EC.02.02.01, EP 9) | PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure |  | 6
EC.02.02.01 EP 8 | Hazardous materials and waste | Disposal of hazardous medications |  | Consolidated (EC.02.02.01, EP 3; EC.02.02.01, EP 4; EC.02.02.01, EP 5; EC.02.02.01, EP 6; EC.02.02.01, EP 7; EC.02.02.01, EP 8; EC.02.02.01, EP 9) | PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure |  | 7
EC.02.02.01 EP 9 | Hazardous materials and waste | Hazardous gases and vapors | NFPA 99-2012: 9.3.8; 9.3.9 | Consolidated (EC.02.02.01, EP 3; EC.02.02.01, EP 4; EC.02.02.01, EP 5; EC.02.02.01, EP 6; EC.02.02.01, EP 7; EC.02.02.01, EP 8; EC.02.02.01, EP 9) | PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure |  | 7
EC.02.02.01 EP 10 | Hazardous materials and waste | Monitor hazardous gas and vapor levels |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure |  | 8
EC.02.02.01 EP 11 | Hazardous materials and waste | Permits, licenses, manifests and safety data sheets |  | Moved | PE.02.01.01 EP 2 | Permits, licenses, manifests and safety data sheets |  | 8
EC.02.02.01 EP 12 | Hazardous materials and waste | Label hazardous materials and waste |  | Moved and revised | PE.02.01.01 EP 3 | Hazardous materials and waste are labeled |  | 8
EC.02.02.01 EP 17 | Hazardous materials and waste | Quarterly dosimetry review (CT, PET, NM, fluoroscopy) |  | Moved and revised | NPG.13.03.01 EP 3 | Quarterly review of staff dosimetry results |  | 8
EC.02.02.01 EP 18 | Hazardous materials and waste | Periodic radiation exposure checks for radiation workers |  | Moved and revised | PE.02.01.01 EP 5 | Radiation workers checked periodically for exposure |  | 9
EC.02.02.01 EP 19 | Hazardous materials and waste | Storage and disposal of trash and regulated medical waste |  | Moved | PE.02.01.01 EP 6 | Routine storage and prompt disposal of trash and regulated medical waste |  | 9
EC.02.03.01 EP 1 | Fire risk and fire response plan | Minimize potential for harm from fire and smoke |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3; PE.04.01.01 EP 1 | Meets the Life Safety Code (NFPA 101-2012 and TIAs); Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 9
EC.02.03.01 EP 4 | Fire risk and fire response plan | Free and unobstructed access to exits (business occupancies) |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 10
EC.02.03.01 EP 9 | Fire risk and fire response plan | Written fire response plan and staff roles | NFPA 101-2012: 18/19.7.1; 7.2 | Moved and revised | PE.03.01.01 EP 4 | Written fire control plans |  | 10
EC.02.03.01 EP 11 | Fire risk and fire response plan | Evaluate surgical fire hazards; fire prevention procedures |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 10
EC.02.03.01 EP 12 | Fire risk and fire response plan | Flammable germicides with electrosurgery, cautery or lasers | NFPA 99-2012: 15.13 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 11
EC.02.03.01 EP 13 | Fire risk and fire response plan | NFPA 99-2012 Chapter 15 fire protection requirements | NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 11
EC.02.03.03 EP 1 | Fire drills | Fire drills: once per shift per quarter (health care); quarterly (ambulatory) | NFPA 101-2012: 18/19 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 11
EC.02.03.03 EP 2 | Fire drills | Fire drills every 12 months in business occupancies where patients are seen |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 12
EC.02.03.03 EP 3 | Fire drills | Drills unannounced, varied, with alarm transmission | NFPA 101-2012: 18/19 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 12
EC.02.03.03 EP 4 | Fire drills | Staff participate according to the fire response plan |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 13
EC.02.03.03 EP 5 | Fire drills | Critique and document fire drills |  | Deleted | N/A | No new EP |  | 13
EC.02.03.03 EP 7 | Fire drills | Annual fire exit drills for operating rooms and surgical suites | NFPA 99-2012: 15.13.3.10.3; NFPA 101-2012: 18/19.7.1.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 14
EC.02.03.03 EP 8 | Fire drills | Annual fire drills for hyperbaric facilities | NFPA 99-2012: 14.2.4.5.4; 14.3.1.4.5; NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 14
EC.02.03.05 EP 1 | Fire protection system testing | Supervisory signal devices (quarterly, semiannual, annual) | NFPA 72-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 14
EC.02.03.05 EP 2 | Fire protection system testing | Water flow devices and valve tamper switches, every 6 months | NFPA 72-2010; NFPA 25-2011 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 15
EC.02.03.05 EP 3 | Fire protection system testing | Duct, heat and smoke detectors and manual pull stations, every 12 months | NFPA 72-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 15
EC.02.03.05 EP 4 | Fire protection system testing | Visual and audible alarms and door-releasing devices, every 12 months | NFPA 72-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 15
EC.02.03.05 EP 5 | Fire protection system testing | Off-site fire responder notification equipment, every 12 months | NFPA 72-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 15
EC.02.03.05 EP 6 | Fire protection system testing | Fire pumps, no-flow: electric monthly, diesel weekly | NFPA 25-2011: 8.3.1; 8.3.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 15
EC.02.03.05 EP 9 | Fire protection system testing | Main drain tests, every 12 months | NFPA 25-2011: 13.2.5; 13.3.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 15
EC.02.03.05 EP 10 | Fire protection system testing | Fire department connections inspected quarterly | NFPA 25-2011: 13.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 15
EC.02.03.05 EP 11 | Fire protection system testing | Fire pumps under flow and supervisory signals, every 12 months | NFPA 25-2011: 8.3.3; 8.3.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 16
EC.02.03.05 EP 12 | Fire protection system testing | Standpipe hydrostatic and flow tests, every 5 years | NFPA 25-2011: 6.3.1; 6.3.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 16
EC.02.03.05 EP 13 | Fire protection system testing | Kitchen fire-extinguishing systems inspected every 6 months | NFPA 96-2011: 11.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 16
EC.02.03.05 EP 14 | Fire protection system testing | Carbon dioxide (12 months), halon (6 months) and other special systems | NFPA 12-2011: 4.8.3.2; NFPA 12A-2009: 6.1; NFPA 11-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 16
EC.02.03.05 EP 15 | Fire protection system testing | Portable fire extinguishers inspected monthly |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 16
EC.02.03.05 EP 16 | Fire protection system testing | Portable fire extinguishers maintained every 12 months by certified individuals | NFPA 10-2010: 7.1.2; 7.2.2; 7.2.4; 7.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 16
EC.02.03.05 EP 17 | Fire protection system testing | Standpipe occupant hoses: hydrostatic test 5 years after install, then every 3 years | NFPA 1962-2008; NFPA 25-2011 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 17
EC.02.03.05 EP 18 | Fire protection system testing | Fire and smoke dampers: 1 year after install, then at least every 6 years | NFPA 90A-2012: 5.4.8; NFPA 80-2010: 19.4; NFPA 105-2010: 6.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 17
EC.02.03.05 EP 19 | Fire protection system testing | Smoke-detection shutdown devices for air handlers, every 12 months | NFPA 90A-2012: 6.4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 17
EC.02.03.05 EP 20 | Fire protection system testing | Sliding and rolling fire doors, every 12 months | NFPA 80-2010: 5.2.14.3; NFPA 105-2010: 5.2.1; 5.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 17
EC.02.03.05 EP 25 | Fire protection system testing | Annual inspection and testing of fire door assemblies | NFPA 101-2012: 7.2.1.5.10.1; 7.2.1.5.11; 7.2.1.15; NFPA 80-2010: 4.8.4; 5.2.1; 5.2.3; 5.2.4; NFPA 105-2010: 5.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 17
EC.02.03.05 EP 27 | Fire protection system testing | Elevators with firefighters' emergency operations, monthly | NFPA 101-2012: 9.4.3; 9.4.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 17
EC.02.03.05 EP 28 | Fire protection system testing | ITM documentation: 7 required fields | NFPA 25-2011: 4.3; 4.4; NFPA 72-2010: 14.2.1; 14.2.2; 14.2.3; 14.2.4 | Moved and revised | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 18
EC.02.04.01 EP 2 | Medical equipment management | Medical equipment inventory |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 18
EC.02.04.01 EP 3 | Medical equipment management | High-risk medical equipment identified |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 18
EC.02.04.01 EP 4 | Medical equipment management | Written ITM activities and frequencies (100% completion) |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 18
EC.02.04.01 EP 5 | Medical equipment management | Manufacturer recommendations for specified equipment (deemed status) |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 18
EC.02.04.01 EP 6 | Medical equipment management | Written criteria for alternate maintenance (AEM) |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 19
EC.02.04.01 EP 7 | Medical equipment management | Equipment in the AEM program identified |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 19
EC.02.04.01 EP 9 | Medical equipment management | Procedures when medical equipment fails |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 19
EC.02.04.01 EP 10 | Medical equipment management | Imaging quality control activities and frequencies |  | Deleted | N/A | No new EP |  | 19
EC.02.04.01 EP 11 | Medical equipment management | Safe Medical Devices Act reporting |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 19
EC.02.04.03 EP 1 | Medical equipment ITM | Safety, operational and functional checks before initial use |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 19
EC.02.04.03 EP 2 | Medical equipment ITM | ITM of all high-risk equipment |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 20
EC.02.04.03 EP 3 | Medical equipment ITM | ITM of non-high-risk equipment |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 20
EC.02.04.03 EP 4 | Medical equipment ITM | Sterilizer performance testing and maintenance |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 20
EC.02.04.03 EP 5 | Medical equipment ITM | Hemodialysis water testing and equipment maintenance |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 20
EC.02.04.03 EP 8 | Medical equipment ITM | Labeling of equipment for oxygen-enriched atmospheres | NFPA 99-2012: 11.5.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 20
EC.02.04.03 EP 10 | Medical equipment ITM | Hyperbaric facilities comply with NFPA 99-2012 Chapter 14 | NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1; PE.04.01.01 EP 2 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs); Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 3 (7 documentation fields) removed. Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 20
EC.02.04.03 EP 16 | Medical equipment ITM | Annual inspection, testing and calibration of nuclear medicine equipment |  | Consolidated (EC.02.04.03, EP 16; EC.02.04.03, EP 23) | PE.05.01.01 EP 1 | Annual nuclear medicine imaging equipment inspection, testing and calibration by a physicist |  | 21
EC.02.04.03 EP 18 | Medical equipment ITM | Maintain quality of CT, PET, MRI and NM images |  | Deleted | N/A | No new EP |  | 21
EC.02.04.03 EP 20 | Medical equipment ITM | Annual CT radiation dose measurement |  | Moved and revised | NPG.13.03.01 EP 4 | Annual CT radiation dose measurement |  | 21
EC.02.04.03 EP 21 | Medical equipment ITM | Annual CT performance evaluation |  | Moved and revised | NPG.13.03.01 EP 5 | Annual CT equipment performance evaluation |  | 22
EC.02.04.03 EP 22 | Medical equipment ITM | Annual MRI performance evaluation |  | Moved and revised | NPG.13.03.01 EP 6 | Annual MRI equipment performance evaluation |  | 22
EC.02.04.03 EP 23 | Medical equipment ITM | Annual nuclear medicine performance evaluation |  | Consolidated (EC.02.04.03, EP 16; EC.02.04.03, EP 23) | PE.05.01.01 EP 1 | Annual nuclear medicine imaging equipment inspection, testing and calibration by a physicist |  | 23
EC.02.04.03 EP 24 | Medical equipment ITM | Annual PET performance evaluation |  | Moved and revised | PE.05.01.01 EP 2 | Annual PET imaging equipment performance evaluation |  | 23
EC.02.04.03 EP 25 | Medical equipment ITM | Annual testing of image acquisition display monitors |  | Moved and revised | PE.05.01.01 EP 3 | Annual testing of image acquisition display monitors |  | 23
EC.02.04.03 EP 26 | Medical equipment ITM | Anesthesia apparatus maintenance and testing | NFPA 99-2012: 11.4.1.3; 11.5.1.3; 11.6.2.5; 11.6.2.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 24
EC.02.04.03 EP 27 | Medical equipment ITM | Electrical equipment in the patient care vicinity (NFPA 99 Chapter 10) | NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 24
EC.02.04.03 EP 34 | Medical equipment ITM | Annual fluoroscopic equipment performance evaluation |  | Moved | PE.05.01.01 EP 4 | Annual fluoroscopic equipment performance evaluation |  | 24
EC.02.05.01 EP 1 | Utility systems management | Design and install utility systems to NFPA codes |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 25
EC.02.05.01 EP 2 | Utility systems management | New and modified systems meet NFPA 99 Categories 1 to 4 | NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 25
EC.02.05.01 EP 3 | Utility systems management | Inventory of utility system operating components |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 25
EC.02.05.01 EP 4 | Utility systems management | High-risk utility components identified on the inventory |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 26
EC.02.05.01 EP 5 | Utility systems management | Written ITM activities and frequencies for utility components | NFPA 99-2012: 6.4.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 26
EC.02.05.01 EP 6 | Utility systems management | Manufacturer recommendations for specified utility components (deemed status) |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 26
EC.02.05.01 EP 7 | Utility systems management | Written criteria for alternate maintenance of utility components |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 26
EC.02.05.01 EP 8 | Utility systems management | Utility components in the AEM program identified |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 26
EC.02.05.01 EP 9 | Utility systems management | Utility system controls labeled | NFPA 101-2012: 18/19.3.4.1; 9.6.1.3; NFPA 72-2010: 10.5.5.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 27
EC.02.05.01 EP 10 | Utility systems management | Written procedures for utility system disruptions |  | Consolidated (EC.02.05.01, EP 10; EC.02.05.01, EP 11; EC.02.05.01, EP 13) | NPG.11.03.01 EP 1 | Written procedures for responding to utility system disruptions |  | 27
EC.02.05.01 EP 11 | Utility systems management | Procedures for shutting off malfunctioning systems and notifying staff |  | Consolidated (EC.02.05.01, EP 10; EC.02.05.01, EP 11; EC.02.05.01, EP 13) | NPG.11.03.01 EP 1 | Written procedures for responding to utility system disruptions |  | 27
EC.02.05.01 EP 12 | Utility systems management | Emergency clinical interventions during utility disruptions |  | Deleted | N/A | No new EP |  | 27
EC.02.05.01 EP 13 | Utility systems management | Respond to utility disruptions as described in procedures |  | Consolidated (EC.02.05.01, EP 10; EC.02.05.01, EP 11; EC.02.05.01, EP 13) | NPG.11.03.01 EP 1 | Written procedures for responding to utility system disruptions |  | 27
EC.02.05.01 EP 15 | Utility systems management | Critical care ventilation: pressure relationships, air changes, filtration, temperature, humidity | NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 27
EC.02.05.01 EP 16 | Utility systems management | Non-critical care ventilation: pressure, temperature and humidity |  | Moved and revised | PE.04.01.01 EP 3 | Ventilation, lighting and temperature control in pharmaceutical, patient care and food preparation areas |  | 28
EC.02.05.01 EP 17 | Utility systems management | Map the distribution of utility systems |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 28
EC.02.05.01 EP 18 | Utility systems management | Medical gas storage, transfer and manifold rooms |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 28
EC.02.05.01 EP 19 | Utility systems management | Emergency power supply equipment and environment maintained | NFPA 99-2012: 9.3.10 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 29
EC.02.05.01 EP 20 | Utility systems management | Operating rooms treated as wet procedure locations unless assessed otherwise | NFPA 99-2012: 6.3.2.2.8.4; 6.3.2.2.8.7; 6.4.4.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 29
EC.02.05.01 EP 21 | Utility systems management | Electrical distribution based on NFPA 99 risk categories | NFPA 99-2012: 3.3.138; 6.3.2.2.10; 6.6.2.2.2; 6.6.3.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 29
EC.02.05.01 EP 22 | Utility systems management | Hospital-grade receptacles at patient beds and anesthetizing locations | NFPA 99-2012: 6.3.2; 6.3.3; 6.3.4; 6.4.2.2.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 29
EC.02.05.01 EP 23 | Utility systems management | Power strips in the patient care vicinity | NFPA 99-2012: 10.2.3.6; 10.2.4; NFPA 99-2012: 10.2.3.6; NFPA 99-2012: 3.3.138 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 30
EC.02.05.01 EP 24 | Utility systems management | Extension cords not used as a substitute for fixed wiring | NFPA 99-2012: 10.2.3.6; 10.2.4; NFPA 70-2011: 400 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 30
EC.02.05.01 EP 25 | Utility systems management | Anesthetizing locations: zone valves and medical gas and vacuum requirements | NFPA 101-2012: 8.7; NFPA 99-2012; NFPA 101-2012: 18/19.3.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3; PE.04.01.01 EP 1 | Meets the Life Safety Code (NFPA 101-2012 and TIAs); Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 30
EC.02.05.01 EP 26 | Utility systems management | Anesthetizing locations: essential electrical system critical branch power | NFPA 101-2012: 8.7; NFPA 99-2012; NFPA 101-2012: 18/19.3.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3; PE.04.01.01 EP 1 | Meets the Life Safety Code (NFPA 101-2012 and TIAs); Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 31
EC.02.05.01 EP 27 | Utility systems management | Engineered smoke control systems per NFPA 92-2012 | NFPA 92-2012; NFPA 101-2012: 19.7.7.1; NFPA 101-2012: 18/19 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3; PE.04.01.01 EP 1 | Meets the Life Safety Code (NFPA 101-2012 and TIAs); Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 32
EC.02.05.02 EP 1 | Water management program | Water management program: responsible individual or team |  | Moved | PE.04.01.05 EP 1 | Water management program: responsible individual or team |  | 33
EC.02.05.02 EP 2 | Water management program | Water management program: system diagram and risk assessment |  | Moved | PE.04.01.05 EP 2 | Water management program: system diagram and risk assessment |  | 33
EC.02.05.02 EP 3 | Water management program | Water management program: monitoring results and corrective actions |  | Moved and revised | PE.04.01.05 EP 3 | Water management program: monitoring results and corrective actions |  | 34
EC.02.05.02 EP 4 | Water management program | Water management program: annual review and review after changes |  | Moved and revised | PE.04.01.05 EP 4 | Water management program: annual review and review after changes |  | 34
EC.02.05.03 EP 1 | Emergency and essential electrical power | Type 1 or Type 3 essential electrical system (facilities built or changed since 1983) | NFPA 99-2012: 6.4.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 34
EC.02.05.03 EP 2 | Emergency and essential electrical power | Emergency power within 10 seconds: alarm systems | NFPA 99-2012: 6.4.1.1; 6.4.2.2; NFPA 110-2010: 4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 34
EC.02.05.03 EP 3 | Emergency and essential electrical power | Emergency power within 10 seconds: exit route and exit sign illumination | NFPA 99-2012: 6.4.1.1; 6.4.2.2; NFPA 110-2010: 4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 35
EC.02.05.03 EP 4 | Emergency and essential electrical power | Life safety branch power for egress lighting and exit signs in new buildings with life support systems | NFPA 101-2012: 18.2.9.2; 18.2.10.5; NFPA 99-2012: 6.4.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 35
EC.02.05.03 EP 5 | Emergency and essential electrical power | Emergency power within 10 seconds: emergency communication systems | NFPA 99-2012: 6.4.2.2; NFPA 110-2010: 4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 35
EC.02.05.03 EP 6 | Emergency and essential electrical power | Emergency power within 10 seconds: equipment whose failure could harm patients | NFPA 99-2012: 6.4.1.1; 6.4.2.2; NFPA 110-2010: 4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 35
EC.02.05.03 EP 7 | Emergency and essential electrical power | Emergency power within 10 seconds: areas where power loss could harm patients | NFPA 99-2012: 6.4.1.1; 6.4.2; NFPA 110-2010: 4.1 | Consolidated (EC.02.05.03, EP 7; EC.02.05.03, EP 16) | PE.04.01.03 EP 1 | Emergency power and lighting in operating, recovery, intensive care and emergency rooms and stairwells |  | 35
EC.02.05.03 EP 11 | Emergency and essential electrical power | Emergency lighting at generator locations; remote manual stop and annunciator | NFPA 99-2012: 6.4.1.1.6; 6.4.1.1.17; 6.4.2.2; NFPA 110-2010: 5.6.5.6; 7.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 35
EC.02.05.03 EP 12 | Emergency and essential electrical power | Equipment on emergency power is energized as designed | NFPA 99-2012: 6.4.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 36
EC.02.05.03 EP 13 | Emergency and essential electrical power | Emergency power for selected elevators | NFPA 99-2012: 6.4.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 36
EC.02.05.03 EP 14 | Emergency and essential electrical power | Emergency backup for essential medication dispensing equipment |  | Moved and revised | NPG.11.03.01 EP 2 | Emergency backup for essential medication dispensing equipment |  | 36
EC.02.05.03 EP 15 | Emergency and essential electrical power | Emergency backup for essential medication refrigeration |  | Moved and revised | NPG.11.03.01 EP 3 | Emergency backup for essential medication refrigeration |  | 36
EC.02.05.03 EP 16 | Emergency and essential electrical power | Battery lamps and flashlights where emergency power is not provided |  | Consolidated (EC.02.05.03, EP 7; EC.02.05.03, EP 16) | PE.04.01.03 EP 1 | Emergency power and lighting in operating, recovery, intensive care and emergency rooms and stairwells |  | 36
EC.02.05.05 EP 1 | Utility system ITM | Manage risks (air quality, infection control, noise, dust) during repairs and maintenance |  | Moved and revised | PE.04.01.03 EP 4 | Managing risks (air quality, infection control, utilities, noise, dust) during repairs and maintenance |  | 37
EC.02.05.05 EP 2 | Utility system ITM | Test utility components before initial use (non-deemed) |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 37
EC.02.05.05 EP 4 | Utility system ITM | ITM of high-risk utility components |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 37
EC.02.05.05 EP 5 | Utility system ITM | ITM of infection control utility components |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 37
EC.02.05.05 EP 6 | Utility system ITM | ITM of non-high-risk utility components |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 37
EC.02.05.05 EP 7 | Utility system ITM | Line isolation monitors tested monthly | NFPA 99-2012: 6.3.2.6.3.6; NFPA 99-2012: 6.3.3.3.2; NFPA 99-2012: 6.3.2; 6.3.3; 6.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 37
EC.02.05.05 EP 8 | Utility system ITM | NFPA 99 electrical and HVAC requirements | NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 37
EC.02.05.07 EP 1 | Emergency power testing | Emergency lighting and exit signs: monthly 30-second functional test | NFPA 101-2012: 7.9.3; 7.10.9; NFPA 99-2012: 6.3.2.2.11.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 38
EC.02.05.07 EP 2 | Emergency power testing | Battery-powered egress lighting: annual 1.5-hour test | NFPA 101-2012: 7.9.3; 7.10.9; NFPA 99-2012: 6.3.2.2.11.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 38
EC.02.05.07 EP 3 | Emergency power testing | SEPSS tests: Level 1 monthly, Level 2 quarterly, plus annual test |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 38
EC.02.05.07 EP 4 | Emergency power testing | Weekly emergency power supply system inspection, including batteries | NFPA 110-2010: 8.3.1; 8.3.3; 8.3.4; 8.3.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 38
EC.02.05.07 EP 5 | Emergency power testing | Monthly generator load test, 30 continuous minutes | NFPA 99-2012: 6.4.4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 39
EC.02.05.07 EP 6 | Emergency power testing | Diesel generator monthly load criteria or annual supplemental load test | NFPA 99-2012: 6.4.4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 39
EC.02.05.07 EP 7 | Emergency power testing | Monthly automatic and manual transfer switch tests | NFPA 99-2012: 6.4.4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 39
EC.02.05.07 EP 8 | Emergency power testing | Annual fuel quality test to ASTM standards | NFPA 110-2010: 8.3.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 39
EC.02.05.07 EP 9 | Emergency power testing | Generator 4-hour test every 36 months | NFPA 110-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 39
EC.02.05.07 EP 10 | Emergency power testing | 36-month diesel generator test load requirements | NFPA 110-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 39
EC.02.05.07 EP 11 | Emergency power testing | All other emergency power requirements of NFPA 99, NFPA 110 and NFPA 101 | NFPA 99-2012; NFPA 110-2010; NFPA 101-2012 | Moved and revised | PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | Since March 1, 2026: note added to implement emergency power ITM per NFPA 99, NFPA 110 and NFPA 101. | 39
EC.02.05.09 EP 1 | Medical gas and vacuum systems | Medical gas, vacuum, WAGD and air systems designed and installed per NFPA 99 | NFPA 99-2012: 5.1.1.1; 5.2.1; 5.3.1.1; 5.3.1.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 40
EC.02.05.09 EP 2 | Medical gas and vacuum systems | Medical gas and vacuum alarm systems | NFPA 99-2012: 5.1.9; 5.2.9; 5.3.6.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 40
EC.02.05.09 EP 3 | Medical gas and vacuum systems | Containers, cylinders and tanks per NFPA 99 | NFPA 99-2012: 5.1.3.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 40
EC.02.05.09 EP 4 | Medical gas and vacuum systems | Door labeling for positive pressure gas locations | NFPA 99-2012: 5.1.3.1.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 41
EC.02.05.09 EP 5 | Medical gas and vacuum systems | Precautionary signs at cylinder storage rooms |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 41
EC.02.05.09 EP 6 | Medical gas and vacuum systems | Cylinder empty threshold and storage requirements by volume | NFPA 99-2012: 11.6.2; NFPA 99-2012: 5.1.3.1; 5.1.3.2.3; 5.2.3.1; 5.3.10 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 41
EC.02.05.09 EP 7 | Medical gas and vacuum systems | ITM of critical medical gas and vacuum components | NFPA 99-2012: 5.1.14.2; 5.1.15; 5.2.14; 5.3.13 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 42
EC.02.05.09 EP 8 | Medical gas and vacuum systems | Bulk oxygen systems in a locked enclosure | NFPA 99-2012: 5.1.3.5.12 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 42
EC.02.05.09 EP 9 | Medical gas and vacuum systems | Emergency oxygen supply connection | NFPA 99-2012: 5.1.3.5.13 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 42
EC.02.05.09 EP 10 | Medical gas and vacuum systems | Piped medical gas testing after installation, modification or breach | NFPA 99-2012: 5.1.2; 5.1.4; 5.1.14.4.1; 5.1.14.4.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | Since March 1, 2026: Note 1 requires 7 documentation fields for fire and smoke detection, alarm and extinguishing system testing; Note 2 covers all other equipment (manufacturer recommendations or AEM). | 43
EC.02.05.09 EP 11 | Medical gas and vacuum systems | Shutoff valves accessible and identified; piping labeled | NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 43
EC.02.05.09 EP 12 | Medical gas and vacuum systems | Cylinder policy: labeling, handling, transport and segregation | NFPA 99-2012: 11.5.3.1; NFPA 99-2012: 11.6.1; 11.6.2; 11.6.5; 11.7.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 43
EC.02.05.09 EP 13 | Medical gas and vacuum systems | No transfilling in patient care rooms | NFPA 99-2012: 11.7.2; NFPA 99-2012: 11.5.2.2; 11.5.2.3.1; 11.5.2.3.2; 11.7.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 43
EC.02.05.09 EP 14 | Medical gas and vacuum systems | All other NFPA 99 gas and vacuum requirements | NFPA 99-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 44
EC.02.06.01 EP 1 | Interior spaces | Interior spaces meet patient needs and are safe and suitable |  | Split (PE.01.01.01, EP 1; PE.01.01.01, EP 2) | PE.01.01.01 EP 1 | Building constructed, arranged and maintained for safe access and patient safety |  | 44
EC.02.06.01 EP 1 | Interior spaces | Interior spaces meet patient needs and are safe and suitable |  | Split (PE.01.01.01, EP 1; PE.01.01.01, EP 2) | PE.01.01.01 EP 2 | Adequate space and facilities for the services provided |  | 44
EC.02.06.01 EP 11 | Interior spaces | Lighting suitable for care, treatment and services |  | Deleted | N/A | No new EP |  | 44
EC.02.06.01 EP 20 | Interior spaces | Areas used by patients are clean and free of offensive odors |  | Consolidated (EC.02.06.01, EP 20) | PE.01.01.01 EP 3 | Premises are clean and orderly |  | 45
EC.02.06.01 EP 26 | Interior spaces | Furnishings and equipment safe and in good repair |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.01.01.01 EP 2 | Adequate space and facilities for the services provided |  | 45
EC.02.06.05 EP 1 | Construction and renovation | Design criteria for new, altered or renovated space | NFPA 99-2012; NFPA 101-2012; NFPA 110-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3; PE.04.01.01 EP 1 | Meets the Life Safety Code (NFPA 101-2012 and TIAs); Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 45
EC.02.06.05 EP 2 | Construction and renovation | Preconstruction risk assessment |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.01.01.01 EP 1 | Building constructed, arranged and maintained for safe access and patient safety |  | 46
EC.02.06.05 EP 3 | Construction and renovation | Act on the assessment to minimize construction risks |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.01.01.01 EP 1 | Building constructed, arranged and maintained for safe access and patient safety |  | 46
EC.02.06.05 EP 4 | Construction and renovation | Shielding review before new imaging equipment or room changes (CT, PET, NM) |  | Deleted | N/A | No new EP |  | 46
EC.02.06.05 EP 6 | Construction and renovation | Imaging room radiation survey after construction (CT, PET, NM) |  | Deleted | N/A | No new EP |  | 46
EC.03.01.01 EP 1 | Staff knowledge and competency | Staff who maintain and use equipment and systems are trained |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | HR.11.03.01 EP 1 | Ongoing staff education and training, documented |  | 47
EC.03.01.01 EP 2 | Staff knowledge and competency | Staff can describe actions to take in an environment of care incident |  | Deleted | N/A | No new EP |  | 47
EC.04.01.01 EP 1 | Monitoring the environment | Process to monitor, report and investigate environment issues |  | Moved and revised | NPG.11.01.01 EP 3 | Monitoring, reporting and investigating injuries, illnesses, property damage and safety incidents |  | 47
EC.04.01.01 EP 3 | Monitoring the environment | Report and investigate: injuries to patients or others |  | Deleted | N/A | No new EP |  | 47
EC.04.01.01 EP 4 | Monitoring the environment | Report and investigate: occupational illnesses and staff injuries |  | Deleted | N/A | No new EP |  | 47
EC.04.01.01 EP 5 | Monitoring the environment | Report and investigate: property damage |  | Deleted | N/A | No new EP |  | 47
EC.04.01.01 EP 6 | Monitoring the environment | Report and investigate: safety and security incidents |  | Deleted | N/A | No new EP |  | 47
EC.04.01.01 EP 8 | Monitoring the environment | Report and investigate: hazardous materials and waste problems |  | Deleted | N/A | No new EP |  | 47
EC.04.01.01 EP 9 | Monitoring the environment | Report and investigate: fire safety problems |  | Deleted | N/A | No new EP |  | 48
EC.04.01.01 EP 10 | Monitoring the environment | Report and investigate: medical and laboratory equipment problems |  | Deleted | N/A | No new EP |  | 48
EC.04.01.01 EP 11 | Monitoring the environment | Report and investigate: utility system problems |  | Deleted | N/A | No new EP |  | 48
EC.04.01.01 EP 15 | Monitoring the environment | Annual evaluation of each environment of care management plan |  | Deleted | N/A | No new EP |  | 48
EC.04.01.03 EP 2 | Analyzing environment data | Use data analysis to identify environmental safety improvements |  | Deleted | N/A | No new EP |  | 48
EC.04.01.05 EP 1 | Improving the environment | Act on identified environmental safety improvements |  | Deleted | N/A | No new EP |  | 48
LS.01.01.01 EP 1 | Life Safety Code management, drawings and SOC | Assign an individual to assess Life Safety Code compliance and manage the SOC |  | Deleted | N/A | No new EP |  | 94
LS.01.01.01 EP 2 | Life Safety Code management, drawings and SOC | Building assessment for Life Safety Code compliance |  | Deleted | N/A | No new EP |  | 95
LS.01.01.01 EP 3 | Life Safety Code management, drawings and SOC | Current, accurate fire safety drawings |  | Moved | PE.03.01.01 EP 1 | Current, accurate fire safety drawings with square footage |  | 95
LS.01.01.01 EP 4 | Life Safety Code management, drawings and SOC | Survey-Related Plan for Improvement (SPFI): 60-day time frame | NFPA 101-2012: 1.4 | Deleted | N/A | No new EP |  | 95
LS.01.01.01 EP 5 | Life Safety Code management, drawings and SOC | Evidence of state or local fire agency inspections and approvals |  | Moved and revised | PE.03.01.01 EP 5 | Written evidence of state or local fire agency inspection and approval |  | 95
LS.01.01.01 EP 6 | Life Safety Code management, drawings and SOC | Do not remove or reduce required life safety features | NFPA 101-2012: 4.6.12.2; 4.6.12.3; 18/19.7.9 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 95
LS.01.01.01 EP 7 | Life Safety Code management, drawings and SOC | Basic Building Information in the Statement of Conditions |  | Moved | PE.03.01.01 EP 2 | Current Basic Building Information in the Statement of Conditions |  | 96
LS.01.01.01 EP 8 | Life Safety Code management, drawings and SOC | Comply with the Life Safety Code (NFPA 101-2012 and TIAs) | NFPA 101-2012 | Moved and revised | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 96
LS.01.02.01 EP 1 | Interim life safety measures (ILSM) | Written ILSM policy |  | Moved and revised | PE.03.02.01 EP 1 | Written interim life safety measures (ILSM) policy |  | 96
LS.01.02.01 EP 2 | Interim life safety measures (ILSM) | ILSM: fire watch or evacuation when fire alarm or sprinkler systems are impaired | NFPA 101-2012: 9.6.1.6; 9.7.6; NFPA 25-2011: 15.5.2 | Moved and revised | PE.03.01.01 EP 8 | Evacuation or fire watch when sprinklers are out for more than 10 hours |  | 97
LS.01.02.01 EP 2 | Interim life safety measures (ILSM) | ILSM: fire watch or evacuation when fire alarm or sprinkler systems are impaired | NFPA 101-2012: 9.6.1.6; 9.7.6; NFPA 25-2011: 15.5.2 | Split (PE.03.01.01, EP 8; PE.03.02.01, EP 2) | PE.03.02.01 EP 2 | ILSM: evacuation, or fire department notification and fire watch, when the fire alarm is out more than 4 of 24 hours |  | 97
LS.01.02.01 EP 3 | Interim life safety measures (ILSM) | ILSM: signage for alternate exits |  | Moved and revised | PE.03.02.01 EP 3 | ILSM: signage for alternate exits |  | 97
LS.01.02.01 EP 4 | Interim life safety measures (ILSM) | ILSM: daily inspection of exits in affected areas |  | Moved and revised | PE.03.02.01 EP 4 | ILSM: daily inspection of exits in affected areas |  | 97
LS.01.02.01 EP 5 | Interim life safety measures (ILSM) | ILSM: temporary equivalent fire alarm and detection systems |  | Moved and revised | PE.03.02.01 EP 5 | ILSM: temporary equivalent fire alarm and detection systems |  | 97
LS.01.02.01 EP 6 | Interim life safety measures (ILSM) | ILSM: additional firefighting equipment |  | Moved and revised | PE.03.02.01 EP 6 | ILSM: additional firefighting equipment |  | 97
LS.01.02.01 EP 7 | Interim life safety measures (ILSM) | ILSM: smoke-tight temporary construction partitions |  | Moved and revised | PE.03.02.01 EP 7 | ILSM: smoke-tight or noncombustible temporary construction partitions |  | 97
LS.01.02.01 EP 8 | Interim life safety measures (ILSM) | ILSM: increased surveillance |  | Moved and revised | PE.03.02.01 EP 8 | ILSM: increased surveillance |  | 97
LS.01.02.01 EP 9 | Interim life safety measures (ILSM) | ILSM: storage, housekeeping and debris removal |  | Moved and revised | PE.03.02.01 EP 9 | ILSM: storage, housekeeping and debris removal |  | 98
LS.01.02.01 EP 10 | Interim life safety measures (ILSM) | ILSM: additional training on firefighting equipment |  | Moved and revised | PE.03.02.01 EP 10 | ILSM: additional training on firefighting equipment |  | 98
LS.01.02.01 EP 11 | Interim life safety measures (ILSM) | ILSM: one additional fire drill per shift per quarter |  | Moved and revised | PE.03.02.01 EP 11 | ILSM: one additional fire drill per shift per quarter |  | 98
LS.01.02.01 EP 12 | Interim life safety measures (ILSM) | ILSM: monthly inspection and testing of temporary systems |  | Moved and revised | PE.03.02.01 EP 12 | ILSM: monthly inspection and testing of temporary systems |  | 98
LS.01.02.01 EP 13 | Interim life safety measures (ILSM) | Education on building deficiencies and construction hazards |  | Moved | PE.03.02.01 EP 13 | Education on building deficiencies and construction hazards |  | 98
LS.01.02.01 EP 14 | Interim life safety measures (ILSM) | Training to compensate for impaired fire safety features |  | Moved | PE.03.02.01 EP 14 | Training to compensate for impaired fire safety features |  | 98
LS.01.02.01 EP 15 | Interim life safety measures (ILSM) | Other ILSMs allowed by policy |  | Moved and revised | PE.03.02.01 EP 15 | Other ILSMs allowed by policy |  | 98
LS.02.01.10 EP 1 | Health care occupancy | Key terms: construction type, sprinklers | NFPA 101-2012: 18/19.1.6; 18.3.5.1; 19.3.5.3; 18/19.3.5.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 98
LS.02.01.10 EP 2 | Health care occupancy | Key terms: rehabilitation | NFPA 101-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 99
LS.02.01.10 EP 3 | Health care occupancy | See Disposition Report for full text | NFPA 101-2012: 43.7; NFPA 101-2012: 18/19.1.1.4.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 99
LS.02.01.10 EP 4 | Health care occupancy | See Disposition Report for full text |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 100
LS.02.01.10 EP 5 | Health care occupancy | Key terms: sprinklers, rehabilitation, smoke compartments | NFPA 101-2012: 18.4.3.2; 18.4.3.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 100
LS.02.01.10 EP 6 | Health care occupancy | Key terms: fire barriers, walls, ceilings | NFPA 101-2012: 8.3.1.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 101
LS.02.01.10 EP 7 | Health care occupancy | Key terms: walls | NFPA 101-2012: 43.8; 18/19.1.1.4; 18/19.1.3.3; 18/19.1.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 101
LS.02.01.10 EP 8 | Health care occupancy | Key terms: construction type | NFPA 101-2012: 8.2.1.3; NFPA 101-2012: 18/19.1.3.5; 8.2.1.3; NFPA 101-2012: 18/19.1.3.4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 102
LS.02.01.10 EP 9 | Health care occupancy | Key terms: fire barriers, doors | NFPA 101-2012: 8.3.3.2; 8.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 102
LS.02.01.10 EP 10 | Health care occupancy | Key terms: sprinklers, exits, stairs | NFPA 101-2012: 7.1.3.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 103
LS.02.01.10 EP 11 | Health care occupancy | Key terms: doors, walls, locks and latches | NFPA 101-2012: 7.2.1.8.2; NFPA 101-2012: 8.3.3.1; 7.2.1.8.2; NFPA 80-2010: 4.8.4.1; 5.2.13.3; 6.3.1.7; 6.4.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 103
LS.02.01.10 EP 12 | Health care occupancy | Key terms: doors, decorations | NFPA 80-2010: 4.1.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 104
LS.02.01.10 EP 13 | Health care occupancy | Key terms: penetrations, walls, dampers | NFPA 101-2012: 8.3.5.7; 9.2.1; NFPA 90A-2012: 5.4.1; 5.4.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 104
LS.02.01.10 EP 14 | Health care occupancy | Key terms: penetrations, walls | NFPA 101-2012: 8.3.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 105
LS.02.01.10 EP 15 | Health care occupancy | Other requirements not covered by the specific EPs |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 105
LS.02.01.20 EP 1 | Health care occupancy | Key terms: doors, locks and latches, elevators | NFPA 101-2012: 7.2.1.6.1; NFPA 101-2012: 7.2.1.6.2; NFPA 101-2012: 18/19.2.2.2.4; 18/19.2.2.2.5; 18/19.2.2.2.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 106
LS.02.01.20 EP 2 | Health care occupancy | Key terms: doors, locks and latches | NFPA 101-2012: 18/19.2.2.2.2; 18/19.2.2.2.5.1; 18/19.2.2.2.5.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 106
LS.02.01.20 EP 3 | Health care occupancy | Key terms: doors, locks and latches | NFPA 101-2012: 7.2.1.14; NFPA 101-2012: 18/19.2.2.2.10.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 107
LS.02.01.20 EP 4 | Health care occupancy | Key terms: doors, locks and latches | NFPA 101-2012: 18/19.2.2.2.10.2; NFPA 80-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 107
LS.02.01.20 EP 5 | Health care occupancy | Key terms: walls, exits | NFPA 101-2012: 7.2.4.3.1; 18/19.2.2.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 108
LS.02.01.20 EP 6 | Health care occupancy | Key terms: doors, exits | NFPA 101-2012: 18.2.2.5.6; 18.2.2.5.4; 19.2.2.5.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 108
LS.02.01.20 EP 7 | Health care occupancy | Key terms: exits, walls | NFPA 101-2012: 7.2.4.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 109
LS.02.01.20 EP 8 | Health care occupancy | Key terms: exits, stairs, walls | NFPA 101-2012: 18/19.2.2.3; 7.2.2.5.2; 7.2.2.6.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 109
LS.02.01.20 EP 9 | Health care occupancy | Key terms: stairs, ramps, exits | NFPA 101-2012: 7.2.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 110
LS.02.01.20 EP 10 | Health care occupancy | Key terms: stairs, exits, doors | NFPA 101-2012: 18/19.2.2.3; 7.2.2.5.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 110
LS.02.01.20 EP 11 | Health care occupancy | See Disposition Report for full text | NFPA 101-2012: 7.3; NFPA 101-2012: 18/19.2.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 111
LS.02.01.20 EP 12 | Health care occupancy | Key terms: exits | NFPA 101-2012: 18/19.2.7; 7.1.7; 7.1.10.1; 7.2.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 111
LS.02.01.20 EP 13 | Health care occupancy | Key terms: exits | NFPA 101-2012: 18/19.2.2.3; 7.1.3.2.3; 7.2.2.5.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 112
LS.02.01.20 EP 14 | Health care occupancy | Key terms: exits, corridors, smoke compartments | NFPA 101-2012: 18/19.2.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 112
LS.02.01.20 EP 15 | Health care occupancy | Key terms: stairs, doors, sprinklers | NFPA 101-2012: 18/19.2.2.2.7; 18/19.2.2.2.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 113
LS.02.01.20 EP 16 | Health care occupancy | Key terms: exits, smoke compartments | NFPA 101-2012: 18/19.2.4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 113
LS.02.01.20 EP 17 | Health care occupancy | Key terms: corridors, exits | NFPA 101-2012: 7.4; NFPA 101-2012: 18/19.2.5.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 114
LS.02.01.20 EP 18 | Health care occupancy | Key terms: exits, corridors | NFPA 101-2012: 18.2.3.4; 18.2.3.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 114
LS.02.01.20 EP 19 | Health care occupancy | Key terms: exits, corridors | NFPA 101-2012: 4.6.12.2; 19.2.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 115
LS.02.01.20 EP 20 | Health care occupancy | Key terms: exits, doors, evacuation | NFPA 101-2012: 19.2.3.6, 19.2.3.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 115
LS.02.01.20 EP 21 | Health care occupancy | Key terms: exits, doors, stairs | NFPA 101-2012: 18.2.3.6; 18.2.3.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 116
LS.02.01.20 EP 22 | Health care occupancy | Key terms: exits, doors |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 116
LS.02.01.20 EP 23 | Health care occupancy | Key terms: doors | NFPA 101-2012: 18.2.2.2.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 117
LS.02.01.20 EP 24 | Health care occupancy | Key terms: corridors, walls | NFPA 101-2012: 18/19.2.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 117
LS.02.01.20 EP 25 | Health care occupancy | Key terms: dead-end corridors, corridors, common path of travel | NFPA 101-2012: 18.2.5.2; NFPA 101-2012: 19.2.5.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 118
LS.02.01.20 EP 26 | Health care occupancy | Key terms: exits, corridors, smoke detection | NFPA 101-2012: 18/19.2.5.6.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 118
LS.02.01.20 EP 27 | Health care occupancy | Key terms: exits, doors | NFPA 101-2012: 18/19.2.5.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 119
LS.02.01.20 EP 28 | Health care occupancy | Key terms: suites, corridors, walls |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 119
LS.02.01.20 EP 29 | Health care occupancy | Key terms: suites | NFPA 101-2012: 18/19.2.5.7.1.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 120
LS.02.01.20 EP 30 | Health care occupancy | Key terms: suites, exits, doors | NFPA 101-2012: 18/19.2.5.7.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 120
LS.02.01.20 EP 31 | Health care occupancy | Key terms: suites, exits, doors | NFPA 101-2012: 18/19.2.5.7.3.2; 18/19.2.5.7.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 121
LS.02.01.20 EP 32 | Health care occupancy | Key terms: suites, electrical, sprinklers | NFPA 101-2012: 9.6.2.9; 19.3.4; 19.3.5.7; 19.3.5.8; NFPA 101-2012: 9.6.2.9; 19.2.5.7.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 121
LS.02.01.20 EP 33 | Health care occupancy | Key terms: suites, smoke detection | NFPA 101-2012: 18.2.5.7.2.3; 18.2.5.7.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 122
LS.02.01.20 EP 34 | Health care occupancy | Key terms: suites | NFPA 101-2012: 18/19.2.5.7.3.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 122
LS.02.01.20 EP 35 | Health care occupancy | Key terms: suites, exits, doors | NFPA 101-2012: 18.2.5.7.2.4; 18.2.5.7.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 123
LS.02.01.20 EP 36 | Health care occupancy | Key terms: suites, exits, doors | NFPA 101-2012: 19.2.5.7.2.4; 19.2.5.7.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 123
LS.02.01.20 EP 37 | Health care occupancy | Key terms: travel distance, exits, suites | NFPA 101-2012: 7.6; NFPA 101-2012: 18/19.2.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 124
LS.02.01.20 EP 38 | Health care occupancy | Key terms: egress lighting, corridors, stairs | NFPA 101-2012: 18/19.2.8; 7.8.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 124
LS.02.01.20 EP 39 | Health care occupancy | Key terms: egress lighting, exits, emergency lighting | NFPA 101-2012: 7.9; NFPA 101-2012: 18/19.2.8; 18/19.2.9.1; 7.8.1.4; 7.9.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 125
LS.02.01.20 EP 40 | Health care occupancy | Key terms: exit signs, exits, egress lighting | NFPA 101-2012: 18/19.2.10; 7.10.1.4; 7.10.1.5.1; 7.10.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 125
LS.02.01.20 EP 41 | Health care occupancy | Key terms: exits, doors, stairs | NFPA 101-2012: 18/19.2.10.1; 7.10.8.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 126
LS.02.01.20 EP 42 | Health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 18/19.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 126
LS.02.01.30 EP 1 | Health care occupancy | Key terms: vertical openings, exits, stairs | NFPA 101-2012: 8.6; 18/19.3.1; 7.1.3.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 127
LS.02.01.30 EP 2 | Health care occupancy | Key terms: hazardous areas, doors, laboratories | NFPA 101-2012: 18.3.2.1; 18.3.2.2; 18.3.2.3; 18.3.2.4 | Moved and revised | PE.03.01.01 EP 6; PE.03.01.01 EP 3 | Positive latching on corridor doors and doors to rooms with flammable materials; Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 127
LS.02.01.30 EP 3 | Health care occupancy | Key terms: hazardous areas, doors, fire barriers | NFPA 101-2012: 19.3.2.1; 19.3.2.2; 19.3.2.3; 19.3.2.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 128
LS.02.01.30 EP 4 | Health care occupancy | Key terms: laboratories | NFPA 101-2012: 8.7; NFPA 101-2012: 18/19.3.2.2; NFPA 99-2012: 15.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3; PE.04.01.01 EP 1 | Meets the Life Safety Code (NFPA 101-2012 and TIAs); Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | Since March 1, 2026: Note 3 (7 documentation fields) removed. | 128
LS.02.01.30 EP 5 | Health care occupancy | Key terms: cooking, smoke compartments, corridors | NFPA 101-2012: 18/19.3.2.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 129
LS.02.01.30 EP 6 | Health care occupancy | Key terms: hand rub dispensers, corridors, suites | NFPA 101-2012: 8.7.3.1; NFPA 101-2012: 18/19.3.2.6 | Consolidated (LS.02.01.30, EP 6; LS.03.01.30, EP 5; LS.05.01.30, EP 3) | PE.03.01.01 EP 7 | Alcohol-based hand rub dispensers installed to prevent inappropriate access |  | 130
LS.02.01.30 EP 7 | Health care occupancy | Key terms: walls, ceilings, interior finishes | NFPA 101-2012: 18/19.3.3; 10.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 130
LS.02.01.30 EP 8 | Health care occupancy | Key terms: corridors, smoke compartments, sprinklers | NFPA 101-2012: 18/19.3.3; 10.2.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 130
LS.02.01.30 EP 9 | Health care occupancy | Key terms: corridors | NFPA 101-2012: 18/19.3.6.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 131
LS.02.01.30 EP 10 | Health care occupancy | Key terms: corridors, walls, ceilings | NFPA 101-2012: 19.3.6.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 131
LS.02.01.30 EP 11 | Health care occupancy | Key terms: corridors, smoke compartments, sprinklers |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 132
LS.02.01.30 EP 12 | Health care occupancy | Key terms: corridors, doors, HVAC | NFPA 101-2012: 18.3.6.3.1; 18.3.6.3.5; 18.3.6.4; 18.3.6.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 132
LS.02.01.30 EP 13 | Health care occupancy | Key terms: corridors, doors, HVAC | NFPA 101-2012: 19.3.6.3.1; 19.3.6.3.2; 19.3.6.3.5; NFPA 101-2012: 19.3.6.3.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 133
LS.02.01.30 EP 14 | Health care occupancy | Key terms: smoke compartments, sprinklers, windows | NFPA 101-2012: 19.3.6.2.7; 8.3.3.8; 8.3.3.9; 8.3.3.11 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 133
LS.02.01.30 EP 15 | Health care occupancy | Key terms: doors, corridors, walls | NFPA 101-2012: 18/19.3.6.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 134
LS.02.01.30 EP 16 | Health care occupancy | Key terms: corridors | NFPA 101-2012: 19.5.2.1; NFPA 90A-2012: 4.3.12.1; 4.3.12.1.3.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 134
LS.02.01.30 EP 17 | Health care occupancy | Key terms: smoke compartments, smoke barriers, travel distance | NFPA 101-2012: 18.3.7.1; 18.3.7.3; 18.3.7.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 135
LS.02.01.30 EP 18 | Health care occupancy | Key terms: smoke compartments, smoke barriers, travel distance | NFPA 101-2012: 19.3.7.1; 19.3.7.3; 19.3.7.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 135
LS.02.01.30 EP 19 | Health care occupancy | Key terms: smoke barriers, ceilings, walls | NFPA 101-2012: 18/19.3.7.3; 8.2.3; 8.5.2; 8.5.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 136
LS.02.01.30 EP 20 | Health care occupancy | Key terms: doors, smoke barriers | NFPA 101-2012: 18.3.7.6; 18/19.3.7.8; 8.5.4.1; NFPA 80-2010: 4.8.4.1; 6.3.1.7.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 136
LS.02.01.30 EP 21 | Health care occupancy | Key terms: smoke compartments, sprinklers, windows | NFPA 101-2012: 19.3.7.6; 8.3.3; 8.5.4.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 137
LS.02.01.30 EP 22 | Health care occupancy | Key terms: dampers, smoke barriers, penetrations | NFPA 101-2012: 18/19.3.7.3; 8.3.5.1; 8.5.5; 8.5.5.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 137
LS.02.01.30 EP 23 | Health care occupancy | Key terms: dampers, ceilings | NFPA 101-2012: 18/19.3.7.3; 8.5.5.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 138
LS.02.01.30 EP 24 | Health care occupancy | Key terms: windows, doors, walls |  | Consolidated (LS.02.01.30, EP 24; LS.02.01.30, EP 25) | PE.03.01.01 EP 9 | Outside window or door in every sleeping room |  | 138
LS.02.01.30 EP 25 | Health care occupancy | Key terms: windows |  | Consolidated (LS.02.01.30, EP 24; LS.02.01.30, EP 25) | PE.03.01.01 EP 9 | Outside window or door in every sleeping room |  | 138
LS.02.01.30 EP 26 | Health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 18/19.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 139
LS.02.01.34 EP 1 | Health care occupancy | Key terms: fire alarm | NFPA 70-2011; NFPA 72-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 139
LS.02.01.34 EP 2 | Health care occupancy | Key terms: fire alarm, smoke detection, walls | NFPA 101-2012: 18/19.3.4.1; 9.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 140
LS.02.01.34 EP 3 | Health care occupancy | Key terms: fire alarm, sprinklers, exits | NFPA 101-2012: 18/19.3.4.2.1; 18/19.3.4.2.2; 9.6.2.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 140
LS.02.01.34 EP 4 | Health care occupancy | Key terms: sprinklers, fire alarm | NFPA 101-2012: 9.6.3; NFPA 101-2012: 18.3.4.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 141
LS.02.01.34 EP 5 | Health care occupancy | Key terms: sprinklers, fire alarm | NFPA 101-2012: 9.6.3; NFPA 101-2012: 19.3.4.3; 9.6.4; 9.7.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 141
LS.02.01.34 EP 6 | Health care occupancy | Key terms: fire alarm | NFPA 72-2010; NFPA 101-2012: 18/19.3.4.4; 9.6.1; 9.6.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 142
LS.02.01.34 EP 7 | Health care occupancy | Key terms: fire alarm | NFPA 101-2012: 9.6.4; NFPA 101-2012: 18/19.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 142
LS.02.01.34 EP 8 | Health care occupancy | Key terms: smoke detection, corridors | NFPA 101-2012; NFPA 101-2012: 18/19.3.4.5.2; 18/19.3.6.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 143
LS.02.01.34 EP 9 | Health care occupancy | Key terms: ceilings, smoke detection | NFPA 101-2012: 18/19.3.4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 143
LS.02.01.34 EP 10 | Health care occupancy | Key terms: fire alarm | NFPA 101-2012: 18/19.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 144
LS.02.01.35 EP 1 | Health care occupancy | Key terms: fire alarm, sprinklers | NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 144
LS.02.01.35 EP 2 | Health care occupancy | Key terms: fire alarm, water | NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 145
LS.02.01.35 EP 3 | Health care occupancy | Key terms: sprinklers | NFPA 101-2012: 18.3.5.1; 19.3.5.3; NFPA 25-2011: 5.2.3.1; 5.2.3.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 145
LS.02.01.35 EP 4 | Health care occupancy | Sprinkler piping not used to support other items | NFPA 25-2011: 5.2.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 146
LS.02.01.35 EP 5 | Health care occupancy | Sprinklers undamaged, free of corrosion, paint and foreign material; escutcheons installed | NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.5; NFPA 25-2011: 5.2.1.1.1; 5.2.1.1.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 146
LS.02.01.35 EP 6 | Health care occupancy | Key terms: sprinklers, walls, ceilings | NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.1.1; NFPA 13-2010: 8.5.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 147
LS.02.01.35 EP 7 | Health care occupancy | Key terms: sprinklers | NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.1.1; NFPA 25-2011: 5.4.1.4; 5.4.1.6; NFPA 13-2010: 6.2.9; 6.2.9.1; 6.2.9.3; 6.2.9.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 147
LS.02.01.35 EP 8 | Health care occupancy | Key terms: sprinklers | NFPA 101-2012: 18/19.3.5.10 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 148
LS.02.01.35 EP 9 | Health care occupancy | Key terms: sprinklers, smoke compartments | NFPA 101-2012: 18.3.5.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 148
LS.02.01.35 EP 10 | Health care occupancy | Key terms: travel distance, fire extinguishers | NFPA 10-2010: 6.2.1.1; 6.1.3.3.1; 6.1.3.4; 6.1.3.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 149
LS.02.01.35 EP 11 | Health care occupancy | Key terms: fire extinguishers, cooking | NFPA 101-2012: 18/19.3.2.5.1; NFPA 96-2011: 10.10.2; NFPA 10-2010: 5.5.5; 6.6.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 149
LS.02.01.35 EP 12 | Health care occupancy | Key terms: cooking | NFPA 101-2012: 18/19.3.2.5.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 150
LS.02.01.35 EP 13 | Health care occupancy | Key terms: cooking, gas and fuel, fire alarm | NFPA 101-2012: 18/19.3.2.5.1; NFPA 96-2011: 10.4; 10.6.1; 10.6.2; 8.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 150
LS.02.01.35 EP 14 | Health care occupancy | All other Life Safety Code automatic sprinkler requirements | NFPA 101-2012: 18/19.3.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 151
LS.02.01.40 EP 1 | Health care occupancy | Key terms: high-rise, sprinklers | NFPA 101-2012: 18/19.4.2; NFPA 101-2012: 11.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 151
LS.02.01.50 EP 1 | Health care occupancy | Key terms: gas and fuel, electrical | NFPA 54-2012; NFPA 70-2012; NFPA 101-2012: 18/19.5.1.1; 9.1.1; 9.1.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 152
LS.02.01.50 EP 2 | Health care occupancy | Key terms: HVAC | NFPA 101-2012: 9.2; NFPA 101-2012: 18/19.5.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 152
LS.02.01.50 EP 3 | Health care occupancy | Key terms: HVAC, gas and fuel | NFPA 101-2012: 18/19.5.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 153
LS.02.01.50 EP 4 | Health care occupancy | Key terms: gas and fuel | NFPA 101-2012: 18/19.5.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 153
LS.02.01.50 EP 5 | Health care occupancy | See Disposition Report for full text | NFPA 101-2012: 18/19.5.2.2; 18/19.5.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 154
LS.02.01.50 EP 6 | Health care occupancy | Key terms: gas and fuel, walls | NFPA 101-2012: 9.2.2; NFPA 101-2012: 9.8; NFPA 101-2012: 18/19.5.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 154
LS.02.01.50 EP 7 | Health care occupancy | Key terms: elevators, smoke detection, travel distance | NFPA 101-2012: 18/19.5.3; 9.4.2; 9.4.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 155
LS.02.01.50 EP 8 | Health care occupancy | Key terms: elevators | NFPA 101-2012: 9.4; NFPA 101-2012: 18/19.5.3; 9.4.2; 9.4.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 155
LS.02.01.50 EP 9 | Health care occupancy | Key terms: doors, trash and linen containers, chutes | NFPA 101-2012: 18/19.5.4; 8.3.3.1; 9.5; NFPA 82-2009: 5.2.3.1.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 156
LS.02.01.50 EP 10 | Health care occupancy | Key terms: trash and linen containers, chutes, doors | NFPA 101-2012: 18/19.5.4; 8.3.3.1; 9.5; NFPA 82-2009: 5.2.3.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 156
LS.02.01.50 EP 11 | Health care occupancy | Key terms: trash and linen containers, chutes, doors | NFPA 101-2012: 18/19.5.4; 9.5; NFPA 82-2009: 5.2.4; 5.2.3.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 157
LS.02.01.50 EP 12 | Health care occupancy | Key terms: sprinklers, trash and linen containers, chutes | NFPA 101-2012: 18/19.5.4.3; 9.7; NFPA 82-2009: 5.2.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 157
LS.02.01.50 EP 13 | Health care occupancy | Key terms: trash and linen containers, chutes, corridors | NFPA 101-2012: 18/19.5.4.4; 19.5.4.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 158
LS.02.01.50 EP 14 | Health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 18/19.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 158
LS.02.01.70 EP 1 | Health care occupancy | Key terms: smoking, oxygen, hazardous areas | NFPA 101-2012: 18/19.7.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 159
LS.02.01.70 EP 2 | Health care occupancy | Key terms: smoking | NFPA 101-2012: 18/19.7.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 159
LS.02.01.70 EP 3 | Health care occupancy | Key terms: curtains and drapes, windows, sprinklers | NFPA 101-2012: 10.3.1; NFPA 101-2012: 18/19.7.5.1; 18/19.3.5.11; 10.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 160
LS.02.01.70 EP 4 | Health care occupancy | Key terms: sprinklers, furnishings | NFPA 101-2012: 10.3.2.1; NFPA 101-2012: 10.3.2.2; NFPA 101-2012: 18/19.7.5.2; 18/19.7.5.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 160
LS.02.01.70 EP 5 | Health care occupancy | Key terms: decorations, walls, ceilings | NFPA 101-2012: 18/19.7.5.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 161
LS.02.01.70 EP 6 | Health care occupancy | Key terms: trash and linen containers, hazardous areas | NFPA 101-2012: 18/19.7.5.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 161
LS.02.01.70 EP 7 | Health care occupancy | See Disposition Report for full text | NFPA 92-2012; NFPA 101-2012: 18/19.7.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 162
LS.02.01.70 EP 8 | Health care occupancy | Key terms: space heaters, smoke compartments, corridors |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 162
LS.02.01.70 EP 9 | Health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 18.7/19.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 163
LS.03.01.10 EP 1 | Ambulatory health care occupancy | Key terms: construction type, sprinklers | NFPA 101-2012: 20/21.1.6.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 163
LS.03.01.10 EP 2 | Ambulatory health care occupancy | Key terms: walls | NFPA 101-2012: 20.1.6.3; 20.1.6.4; 21.1.6.3; 21.1.6.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 164
LS.03.01.10 EP 3 | Ambulatory health care occupancy | Key terms: rehabilitation | NFPA 101-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 164
LS.03.01.10 EP 4 | Ambulatory health care occupancy | Key terms: walls | NFPA 101-2012: 20/21.1.3; 20/21.1.4; 20/21.3.7.1; NFPA 101-2012: 20/21.1.3.2; 20/21.3.7.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 165
LS.03.01.10 EP 5 | Ambulatory health care occupancy | Key terms: fire barriers, walls, ceilings | NFPA 101-2012: 8.3.1.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 165
LS.03.01.10 EP 6 | Ambulatory health care occupancy | Key terms: fire barriers, doors, locks and latches | NFPA 101-2012: 8.3.3.2; 8.3.4.2; NFPA 80-2010: 5.2.13.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 166
LS.03.01.10 EP 7 | Ambulatory health care occupancy | Key terms: doors, walls, locks and latches | NFPA 101-2012: 8.3.3.1; NFPA 80-2010: 4.8.4.1; 5.2.13.3; 6.3.1.7; 6.4.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 166
LS.03.01.10 EP 8 | Ambulatory health care occupancy | Key terms: doors, decorations | NFPA 80-2010: 4.1.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 167
LS.03.01.10 EP 9 | Ambulatory health care occupancy | Key terms: penetrations, walls, dampers | NFPA 101-2012: 8.3.5.7; 9.2.1; NFPA 90A-2012: 5.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 167
LS.03.01.10 EP 10 | Ambulatory health care occupancy | Key terms: penetrations, walls | NFPA 101-2012: 8.3.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 168
LS.03.01.10 EP 11 | Ambulatory health care occupancy | Other requirements not covered by the specific EPs |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 168
LS.03.01.20 EP 1 | Ambulatory health care occupancy | Key terms: doors, locks and latches, elevators | NFPA 101-2012: 7.2.1.6.1; NFPA 101-2012: 7.2.1.6.2; NFPA 101-2012: 20/21.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 169
LS.03.01.20 EP 2 | Ambulatory health care occupancy | Key terms: doors, exits, stairs | NFPA 101-2012: 20/21.2.2.4; 20/21.2.2.5; 7.2.1.8.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 169
LS.03.01.20 EP 3 | Ambulatory health care occupancy | Key terms: exits | NFPA 101-2012: 20/21.2.1; 20/21.2.7; 38/39.2.7; 7.1.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 170
LS.03.01.20 EP 4 | Ambulatory health care occupancy | See Disposition Report for full text | NFPA 101-2012: 7.3; NFPA 101-2012: 20/21.2.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 170
LS.03.01.20 EP 5 | Ambulatory health care occupancy | Key terms: exits, corridors, doors | NFPA 101-2012: 20/21.2.3.2; 2.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 171
LS.03.01.20 EP 6 | Ambulatory health care occupancy | Key terms: exits | NFPA 101-2012: 7.1.10.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 171
LS.03.01.20 EP 7 | Ambulatory health care occupancy | Key terms: exits, doors |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 172
LS.03.01.20 EP 8 | Ambulatory health care occupancy | Key terms: exits, smoke compartments, suites | NFPA 101-2012: 20/21.2.4.1; 2.4.2; 7.4; 38/39.2.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 172
LS.03.01.20 EP 9 | Ambulatory health care occupancy | Key terms: sprinklers, dead-end corridors, corridors | NFPA 101-2012: 20/21.2.5; 38/39.2.5.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 173
LS.03.01.20 EP 10 | Ambulatory health care occupancy | Key terms: travel distance, exits, sprinklers | NFPA 101-2012: 20/21.2.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 173
LS.03.01.20 EP 11 | Ambulatory health care occupancy | Key terms: exits | NFPA 101-2012: 20/21.2.1; 7.2.2.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 174
LS.03.01.20 EP 12 | Ambulatory health care occupancy | Key terms: egress lighting, corridors, stairs | NFPA 101-2012: 20/21.2.8; 7.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 174
LS.03.01.20 EP 13 | Ambulatory health care occupancy | Key terms: egress lighting, exits, emergency lighting | NFPA 101-2012: 7.9; NFPA 101-2012: 20/21.2.8; 7.8.1.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 175
LS.03.01.20 EP 14 | Ambulatory health care occupancy | Key terms: exits, doors, stairs |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 175
LS.03.01.20 EP 15 | Ambulatory health care occupancy | Key terms: exit signs, exits | NFPA 101-2012: 20/21.2.10; 7.10.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 176
LS.03.01.20 EP 16 | Ambulatory health care occupancy | Key terms: egress lighting, emergency lighting, exits | NFPA 99-2012; NFPA 101-2012: 20.2.9.2; NFPA 99-2012: 6.4.2.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 176
LS.03.01.20 EP 17 | Ambulatory health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 20/21.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 177
LS.03.01.30 EP 1 | Ambulatory health care occupancy | Key terms: vertical openings, exits, stairs | NFPA 101-2012: 20/21.3.1; 8.6; 8.6.5; 38/39.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 177
LS.03.01.30 EP 2 | Ambulatory health care occupancy | Key terms: exits, stairs | NFPA 101-2012: 20/21.3.1; 38/39.3.1; 8.6.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 178
LS.03.01.30 EP 3 | Ambulatory health care occupancy | Key terms: hazardous areas, walls, doors | NFPA 101-2012: 20/21.3.2; 38/39.3.2; 8.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 178
LS.03.01.30 EP 4 | Ambulatory health care occupancy | Key terms: laboratories | NFPA 99-2012; NFPA 101-2012: 20/21.3.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 179
LS.03.01.30 EP 5 | Ambulatory health care occupancy | Key terms: hand rub dispensers, corridors, suites | NFPA 101-2012: 8.7.3.1; NFPA 101-2012: 20/21.3.2.6 | Consolidated (LS.02.01.30, EP 6; LS.03.01.30, EP 5; LS.05.01.30, EP 3) | PE.03.01.01 EP 7 | Alcohol-based hand rub dispensers installed to prevent inappropriate access |  | 179
LS.03.01.30 EP 6 | Ambulatory health care occupancy | Key terms: cooking | NFPA 96-2011; NFPA 101-2012: 20/21.3.2.4; 20/21.3.2.5; 9.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 179
LS.03.01.30 EP 7 | Ambulatory health care occupancy | Key terms: walls, ceilings, interior finishes | NFPA 101-2012: 20/21.3.3; 38/39.3.3.2; 10.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 180
LS.03.01.30 EP 8 | Ambulatory health care occupancy | Key terms: exits, corridors | NFPA 101-2012: 20/21.3.3; 10.2.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 180
LS.03.01.30 EP 9 | Ambulatory health care occupancy | Key terms: doors, ceilings, sprinklers | NFPA 101-2012: 20.3.6.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 181
LS.03.01.30 EP 10 | Ambulatory health care occupancy | Key terms: corridors, exits | NFPA 101-2012: 38.3.6.1; NFPA 101-2012: 20.3.6.2; 38.3.6.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 181
LS.03.01.30 EP 11 | Ambulatory health care occupancy | Key terms: doors, locks and latches, windows | NFPA 101-2012: 8.3; NFPA 101-2012: 20/21.3.7.1; 8.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 182
LS.03.01.30 EP 12 | Ambulatory health care occupancy | Key terms: smoke compartments, sprinklers, walls | NFPA 101-2012: 9.7; NFPA 101-2012: 8.3; NFPA 101-2012: 20/21.3.7.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 182
LS.03.01.30 EP 13 | Ambulatory health care occupancy | Key terms: smoke barriers, ceilings, walls | NFPA 101-2012: 20/21.3.7.5; 20/21.3.7.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 183
LS.03.01.30 EP 14 | Ambulatory health care occupancy | Key terms: penetrations, smoke barriers, dampers | NFPA 101-2012: 20/21.3.7.6; 8.5.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 183
LS.03.01.30 EP 15 | Ambulatory health care occupancy | Key terms: windows, smoke barriers, walls | NFPA 101-2012: 20/21.3.7.7, 8.3.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 184
LS.03.01.30 EP 16 | Ambulatory health care occupancy | Key terms: doors, smoke barriers | NFPA 101-2012: 20/21.3.7.9; 20/21.2.2.4; 20.3.7.9; 20.3.7.10 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 184
LS.03.01.30 EP 17 | Ambulatory health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 20/21.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 185
LS.03.01.34 EP 1 | Ambulatory health care occupancy | Key terms: fire alarm | NFPA 70-2012; NFPA 72-2010 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 185
LS.03.01.34 EP 2 | Ambulatory health care occupancy | Key terms: fire alarm, smoke detection, walls | NFPA 101-2012: 20/21.3.4.1; 9.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 186
LS.03.01.34 EP 3 | Ambulatory health care occupancy | Key terms: fire alarm, sprinklers, exits | NFPA 101-2012: 20/21.3.4.2.1; 20/21.3.4.2.2; 9.6.2.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 186
LS.03.01.34 EP 4 | Ambulatory health care occupancy | Key terms: sprinklers, fire alarm | NFPA 101-2012: 9.6.3; NFPA 101-2012: 20.3.4.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 187
LS.03.01.34 EP 5 | Ambulatory health care occupancy | Key terms: sprinklers, fire alarm | NFPA 101-2012: 9.6.3; NFPA 101-2012: 21.3.4.3; 9.6.4; 9.7.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 187
LS.03.01.34 EP 6 | Ambulatory health care occupancy | Key terms: fire alarm | NFPA 72-2010; NFPA 101-2012: 20/21.3.4.4; 9.6.1; 9.6.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 188
LS.03.01.34 EP 7 | Ambulatory health care occupancy | Key terms: fire alarm | NFPA 101-2012: 20/21.3.4.3.2; NFPA 101-2012: 9.6.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 188
LS.03.01.34 EP 8 | Ambulatory health care occupancy | See Disposition Report for full text | NFPA 101-2012: 20/21.3.4.3, 9.6.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 189
LS.03.01.34 EP 9 | Ambulatory health care occupancy | Key terms: fire alarm, evacuation | NFPA 101-2012: 20/21.3.4.3, 9.6.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 189
LS.03.01.34 EP 10 | Ambulatory health care occupancy | Key terms: fire alarm | NFPA 101-2012: 20.3.4/21.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 190
LS.03.01.35 EP 1 | Ambulatory health care occupancy | Key terms: fire alarm, sprinklers | NFPA 101-2012: 20/21.3.5.2; 9.7.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 190
LS.03.01.35 EP 2 | Ambulatory health care occupancy | Key terms: fire alarm, water, sprinklers | NFPA 101-2012: 20/21.3.4.4; 20/21.3.5; 9.7.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 191
LS.03.01.35 EP 3 | Ambulatory health care occupancy | Key terms: sprinklers | NFPA 101-2012: 20/21.3.4.4; NFPA 25-2011: 5.2.1; 5.2.2; 5.2.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 191
LS.03.01.35 EP 4 | Ambulatory health care occupancy | Key terms: sprinklers | NFPA 101-2012: 20/21.3.4.4; NFPA 25-2011: 5.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 192
LS.03.01.35 EP 5 | Ambulatory health care occupancy | Key terms: sprinklers | NFPA 101-2012: 20/21.3.4.4; NFPA 25-2011: 5.2.1; 5.2.2; NFPA 13-2010: 6.2.6.2; 6.2.7.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 192
LS.03.01.35 EP 6 | Ambulatory health care occupancy | Key terms: sprinklers, walls, ceilings | NFPA 101-2012: 20/21.3.4.4; NFPA 13-2010: 8.5.5; 8.5.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 193
LS.03.01.35 EP 7 | Ambulatory health care occupancy | Key terms: sprinklers | NFPA 101-2012: 9.7.1.1; NFPA 13-2010: 6.2.9; 6.2.9.1; 6.2.9.3; 6.2.9.6; NFPA 13-2010: 6.2.9.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 193
LS.03.01.35 EP 10 | Ambulatory health care occupancy | Key terms: travel distance, fire extinguishers | NFPA 10-2010: 6.1.3; 6.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 194
LS.03.01.35 EP 11 | Ambulatory health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 20/21.3.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 194
LS.03.01.40 EP 1 | Ambulatory health care occupancy | Key terms: windowless buildings, windows | NFPA 101-2012: 20/21.4; 11.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 195
LS.03.01.40 EP 2 | Ambulatory health care occupancy | Key terms: high-rise, sprinklers | NFPA 101-2012: 20/21.4; 11.8; 9.7.1.1; NFPA 101-2012: 39.4.2.1; NFPA 101-2012: 11.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 195
LS.03.01.40 EP 3 | Ambulatory health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 20/21.3.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 196
LS.03.01.50 EP 1 | Ambulatory health care occupancy | Key terms: gas and fuel, electrical | NFPA 54-2012; NFPA 70-2012; NFPA 101-2012: 20/21.5.1; 9.1.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 196
LS.03.01.50 EP 2 | Ambulatory health care occupancy | Key terms: HVAC | NFPA 101-2012: 9.2; NFPA 101-2012: 20/21.5.2.1; 9.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 197
LS.03.01.50 EP 3 | Ambulatory health care occupancy | Key terms: HVAC, gas and fuel | NFPA 101-2012: 20/21.5.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 197
LS.03.01.50 EP 4 | Ambulatory health care occupancy | Key terms: gas and fuel | NFPA 101-2012: 20/21.5.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 198
LS.03.01.50 EP 5 | Ambulatory health care occupancy | Key terms: elevators, smoke detection, travel distance | NFPA 101-2012: 20/21.5.3; 9.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 198
LS.03.01.50 EP 6 | Ambulatory health care occupancy | Key terms: elevators | NFPA 101-2012: 20/21.5.3; 9.4.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 199
LS.03.01.50 EP 7 | Ambulatory health care occupancy | Key terms: gas and fuel | NFPA 101-2012: 20/21.5.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 199
LS.03.01.50 EP 8 | Ambulatory health care occupancy | Key terms: HVAC, gas and fuel | NFPA 101-2012: 20/21.5.2.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 200
LS.03.01.50 EP 9 | Ambulatory health care occupancy | Key terms: chutes, walls, doors | NFPA 101-2012: 9.5; NFPA 101-2012: 8.3; NFPA 101-2012: 8.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 200
LS.03.01.50 EP 10 | Ambulatory health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 20/21.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 201
LS.03.01.70 EP 1 | Ambulatory health care occupancy | Key terms: smoking | NFPA 101-2012: 20/21.7.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 201
LS.03.01.70 EP 2 | Ambulatory health care occupancy | Key terms: smoking, oxygen, hazardous areas | NFPA 101-2012: 18/19.7.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 202
LS.03.01.70 EP 3 | Ambulatory health care occupancy | Key terms: curtains and drapes, windows, sprinklers | NFPA 101-2012: 10.3.1; NFPA 101-2012: 18/19.7.5.1; 18/19.3.5.11; 10.3.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 202
LS.03.01.70 EP 4 | Ambulatory health care occupancy | Key terms: sprinklers, furnishings | NFPA 101-2012: 10.3.2.1; NFPA 101-2012: 10.3.2.2; NFPA 101-2012: 20/21.7.5.2; 20/21.7.5.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 203
LS.03.01.70 EP 5 | Ambulatory health care occupancy | Key terms: decorations | NFPA 101-2012: 20/21.7.5.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 203
LS.03.01.70 EP 6 | Ambulatory health care occupancy | Key terms: trash and linen containers, hazardous areas | NFPA 101-2012: 20/21.7.5.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 204
LS.03.01.70 EP 7 | Ambulatory health care occupancy | See Disposition Report for full text | NFPA 92-2012; NFPA 101-2012: 20/21.7.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 204
LS.03.01.70 EP 8 | Ambulatory health care occupancy | Key terms: space heaters, smoke compartments, corridors | NFPA 101-2012: 20/21.7.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 205
LS.03.01.70 EP 9 | Ambulatory health care occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 20/21.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 205
LS.05.01.10 EP 1 | Business occupancy: general requirements and rehabilitation | Key terms: rehabilitation | NFPA 101-2012; NFPA 101-2012: 38/39.1.1.3; 4.6.7 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 206
LS.05.01.10 EP 2 | Business occupancy: general requirements and rehabilitation | Key terms: fire barriers | NFPA 101-2012: 38/39.1.3.2.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 206
LS.05.01.10 EP 3 | Business occupancy: general requirements and rehabilitation | Key terms: fire barriers, doors | NFPA 101-2012: 8.3.4.2; NFPA 80-2010: 5.2.13.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 207
LS.05.01.10 EP 5 | Business occupancy: general requirements and rehabilitation | Key terms: penetrations, walls | NFPA 101-2012: 8.3.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 207
LS.05.01.10 EP 6 | Business occupancy: general requirements and rehabilitation | Key terms: doors, decorations | NFPA 80-2010: 4.1.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 208
LS.05.01.10 EP 7 | Business occupancy: general requirements and rehabilitation | Other requirements not covered by the specific EPs | NFPA 101-2012: 38/39.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 208
LS.05.01.20 EP 1 | Business occupancy | Key terms: stairs, ramps | NFPA 101-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 209
LS.05.01.20 EP 2 | Business occupancy | Key terms: corridors | NFPA 101-2012: 38/39.2.3.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 209
LS.05.01.20 EP 3 | Business occupancy | Key terms: dead-end corridors, corridors, sprinklers | NFPA 101-2012: 38/39.2.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 210
LS.05.01.20 EP 4 | Business occupancy | Key terms: travel distance, exits, sprinklers | NFPA 101-2012: 38/39.2.6 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 210
LS.05.01.20 EP 5 | Business occupancy | Key terms: egress lighting | NFPA 101-2012: 38/39.2.8 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 211
LS.05.01.20 EP 6 | Business occupancy | Key terms: emergency lighting, exits | NFPA 101-2012: 39.2.9 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 211
LS.05.01.20 EP 7 | Business occupancy | Key terms: emergency lighting, exits | NFPA 101-2012: 38.2.9 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 212
LS.05.01.20 EP 8 | Business occupancy | Key terms: doors, locks and latches, exits | NFPA 101-2012: 38/39.2.2.2; 7.2.1.5.3; 7.2.1.6.1; 7.2.1.6.2; NFPA 101-2012 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 212
LS.05.01.20 EP 9 | Business occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 38/39.2 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 213
LS.05.01.30 EP 1 | Business occupancy | Key terms: hazardous areas, walls, doors | NFPA 101-2012: 38/39.3.2; 8.7; NFPA 80-2010: 4.8.4.1; 6.3.1.7; 6.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 213
LS.05.01.30 EP 2 | Business occupancy | Key terms: walls, ceilings, exits |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 214
LS.05.01.30 EP 3 | Business occupancy | Key terms: hand rub dispensers, corridors, suites | NFPA 101-2012: 8.7.3.1 | Consolidated (LS.02.01.30, EP 6; LS.03.01.30, EP 5; LS.05.01.30, EP 3) | PE.03.01.01 EP 7 | Alcohol-based hand rub dispensers installed to prevent inappropriate access |  | 214
LS.05.01.30 EP 4 | Business occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 38/39.3 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 214
LS.05.01.34 EP 1 | Business occupancy | Key terms: fire alarm, exits, smoke detection | NFPA 101-2012: 39.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 215
LS.05.01.34 EP 2 | Business occupancy | Key terms: fire alarm, exits, smoke detection | NFPA 101-2012: 38.3.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 215
LS.05.01.34 EP 3 | Business occupancy | Key terms: fire alarm | NFPA 101-2012: 38/39.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 216
LS.05.01.34 EP 4 | Business occupancy | See Disposition Report for full text | NFPA 101-2012: 9.6.4; NFPA 101-2012: 38.3.4.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 216
LS.05.01.34 EP 5 | Business occupancy | Key terms: fire alarm | NFPA 101-2012: 9.6.4; NFPA 101-2012: 39.3.4.4 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 217
LS.05.01.35 EP 3 | Business occupancy | Key terms: travel distance, fire extinguishers | NFPA 101-2012: 38/39.3.5; 9.7.4.1 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 217
LS.05.01.35 EP 4 | Business occupancy | Key terms: sprinklers |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 218
LS.05.01.35 EP 5 | Business occupancy | Key terms: sprinklers, walls, ceilings |  | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 218
LS.05.01.35 EP 6 | Business occupancy | Other requirements not covered by the specific EPs | NFPA 101-2012: 38/39.3.5 | Deleted EP; replaced with more direct EP or moved to SPG guidance | PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) |  | 219

## Summary
Where the former EPs landed
Counts update automatically from the Crosswalk tab.
New standard / EP | New requirement (summary) | Former EP rows
PE.01.01.01 EP 1 | Building constructed, arranged and maintained for safe access and patient safety | 6
PE.01.01.01 EP 2 | Adequate space and facilities for the services provided | 2
PE.01.01.01 EP 3 | Premises are clean and orderly | 1
PE.02.01.01 EP 1 | Written, current inventory of hazardous materials and waste | 1
PE.02.01.01 EP 2 | Permits, licenses, manifests and safety data sheets | 1
PE.02.01.01 EP 3 | Hazardous materials and waste are labeled | 1
PE.02.01.01 EP 4 | Policies and procedures to protect people from hazardous materials exposure | 8
PE.02.01.01 EP 5 | Radiation workers checked periodically for exposure | 1
PE.02.01.01 EP 6 | Routine storage and prompt disposal of trash and regulated medical waste | 1
PE.03.01.01 EP 1 | Current, accurate fire safety drawings with square footage | 1
PE.03.01.01 EP 2 | Current Basic Building Information in the Statement of Conditions | 1
PE.03.01.01 EP 3 | Meets the Life Safety Code (NFPA 101-2012 and TIAs) | 252
PE.03.01.01 EP 4 | Written fire control plans | 1
PE.03.01.01 EP 5 | Written evidence of state or local fire agency inspection and approval | 1
PE.03.01.01 EP 6 | Positive latching on corridor doors and doors to rooms with flammable materials | 1
PE.03.01.01 EP 7 | Alcohol-based hand rub dispensers installed to prevent inappropriate access | 3
PE.03.01.01 EP 8 | Evacuation or fire watch when sprinklers are out for more than 10 hours | 1
PE.03.01.01 EP 9 | Outside window or door in every sleeping room | 2
PE.03.02.01 EP 1 | Written interim life safety measures (ILSM) policy | 1
PE.03.02.01 EP 2 | ILSM: evacuation, or fire department notification and fire watch, when the fire alarm is out more than 4 of 24 hours | 1
PE.03.02.01 EP 3 | ILSM: signage for alternate exits | 1
PE.03.02.01 EP 4 | ILSM: daily inspection of exits in affected areas | 1
PE.03.02.01 EP 5 | ILSM: temporary equivalent fire alarm and detection systems | 1
PE.03.02.01 EP 6 | ILSM: additional firefighting equipment | 1
PE.03.02.01 EP 7 | ILSM: smoke-tight or noncombustible temporary construction partitions | 1
PE.03.02.01 EP 8 | ILSM: increased surveillance | 1
PE.03.02.01 EP 9 | ILSM: storage, housekeeping and debris removal | 1
PE.03.02.01 EP 10 | ILSM: additional training on firefighting equipment | 1
PE.03.02.01 EP 11 | ILSM: one additional fire drill per shift per quarter | 1
PE.03.02.01 EP 12 | ILSM: monthly inspection and testing of temporary systems | 1
PE.03.02.01 EP 13 | Education on building deficiencies and construction hazards | 1
PE.03.02.01 EP 14 | Training to compensate for impaired fire safety features | 1
PE.03.02.01 EP 15 | Other ILSMs allowed by policy | 1
PE.04.01.01 EP 1 | Meets the Health Care Facilities Code (NFPA 99-2012 and TIAs) | 41
PE.04.01.01 EP 2 | Maintains essential equipment in safe operating condition | 53
PE.04.01.01 EP 3 | Ventilation, lighting and temperature control in pharmaceutical, patient care and food preparation areas | 1
PE.04.01.03 EP 1 | Emergency power and lighting in operating, recovery, intensive care and emergency rooms and stairwells | 2
PE.04.01.03 EP 3 | Emergency power system and generator requirements of NFPA 99, NFPA 110 and NFPA 101 | 16
PE.04.01.03 EP 4 | Managing risks (air quality, infection control, utilities, noise, dust) during repairs and maintenance | 1
PE.04.01.05 EP 1 | Water management program: responsible individual or team | 1
PE.04.01.05 EP 2 | Water management program: system diagram and risk assessment | 1
PE.04.01.05 EP 3 | Water management program: monitoring results and corrective actions | 1
PE.04.01.05 EP 4 | Water management program: annual review and review after changes | 1
PE.05.01.01 EP 1 | Annual nuclear medicine imaging equipment inspection, testing and calibration by a physicist | 2
PE.05.01.01 EP 2 | Annual PET imaging equipment performance evaluation | 1
PE.05.01.01 EP 3 | Annual testing of image acquisition display monitors | 1
PE.05.01.01 EP 4 | Annual fluoroscopic equipment performance evaluation | 1
NPG.02.04.01 EP 3 | Annual workplace violence worksite analysis | 1
NPG.11.01.01 EP 1 | Controls access to security-sensitive areas | 1
NPG.11.01.01 EP 2 | Security incident policies and procedures, including infant or pediatric abduction | 2
NPG.11.01.01 EP 3 | Monitoring, reporting and investigating injuries, illnesses, property damage and safety incidents | 1
NPG.11.03.01 EP 1 | Written procedures for responding to utility system disruptions | 3
NPG.11.03.01 EP 2 | Emergency backup for essential medication dispensing equipment | 1
NPG.11.03.01 EP 3 | Emergency backup for essential medication refrigeration | 1
NPG.13.03.01 EP 1 | MRI safety risks | 1
NPG.13.03.01 EP 2 | MRI access restriction, supervision and signage | 1
NPG.13.03.01 EP 3 | Quarterly review of staff dosimetry results | 1
NPG.13.03.01 EP 4 | Annual CT radiation dose measurement | 1
NPG.13.03.01 EP 5 | Annual CT equipment performance evaluation | 1
NPG.13.03.01 EP 6 | Annual MRI equipment performance evaluation | 1
HR.11.03.01 EP 1 | Ongoing staff education and training, documented | 1
N/A | No new EP | 33
By disposition
Moved |  | 14
Moved and revised |  | 35
Consolidated |  | 22
Split |  | 3
Deleted EP; replaced or moved to SPG |  | 359
Deleted |  | 32
Total rows |  | 465